## B027-HVAC-EXF-2701
BLDG: KPV ASSET: B027-HVAC-EXF-2701
EAM ASSET INFORMATION:
DESCRIPTION: | OWNING DEPT: | CRITICALITY:
EXHAUST FAN - EXF | Zone 1 | TIER 2
ASSET ID #: | AREA SERVED: | WIP ACCOUNTING CLASS:
B027-HVAC-EXF-2701 | KPV BLDG EXHAUST EAST WING | ZONE1WAC
OLD ASSET ID #: | MAINTAINABLE/ACTIVE | SYSTEM:
B027-HVAC-EXF-1 | Yes | HVAC-EXF
Associated Equipment: Back-up Fan B027-HVAC-EXF-2702
Planned Maintenance Frequencies: 90, 365
Planned Maintenance Activitiey #'s: 502089, 502219
EQUIPMENT DATA:
LOCATION: |  | INSTALL DATE:
N. ROOF LOWER PIT |  | 2004-12-04
FAN MANUFACTURE: | MODEL #: | SERIAL #:
LOREN COOK | 402 CPSA 402 CPS-A | 034S8148240100007011204
CAPACITY: cfm-23,300 / rpm-964 | SIZE: | TYPE:
ELECTRICAL DATA:
MOTOR MANUFACTURE: | SPEC #: | SERIAL #:
BALDOR / EM2531T-G | 40E246W273G1 | Z130200042
HP: 25 | RPM: 1760 | VOLTS: 230 / 460
AMPS: 58 / 29 | FRAME#: 284T | PHASE: 3
ENCLOSURE: OPSB | BEARINGS: 6309 / 6311
MOTOR SHEAVE: 4B56SD / BUSHING - SD- 1 7/8"
PANEL / BREAKER / LOCATION: MCC PHNH1 / EF-1 / N. PENTHOUSE
MECHANICAL DATA:
FAN BEARINGS: DODGE - SCM- 2 3/16" |  | BELTS: BX-92 4 ea
FAN SHEAVE: 4B110SK / BUSHING - SKX- 2 3/16"
LUBRICATION: GREASE - EP-2
RECOMMENDED ACTIVITIES: | FOLLOW LOCK-OUT TAG-OUT PROCEDURES
QUARTERLY: Check operation of unit, valves, dampers, sensors; listen for unusual noise or vibration; Check motor and fan bearings for excessive heat, vibration, lube if necessary; Inspect belts, pulleys for wear, adjust or replace if necessary; Inspect dampers, linkage, lube if necessary; Inspect Ductwork; Check all mounts, welds, connections; Check for loose, broken or missing parts. Clean unit
ANNUAL: Collect and verify all unit data; Verify operation of control systems (BAS or HOA) Perform Quarterly preventative maintenance.
Regulatory or Compliance Requirement:
Safety Hazards:
Notes
Notify building manager and affected areas if shut down is of significant impact to daily operations of tenants